## ATP-Cable_3phase_Bergeron
Mark the first matrix below
From ATPDraw double click cable symbol, Check Cable constant Press RunATP, Copy Z-Matrix from command window with ALT+Mark |  |  | , choose cable symbol, Press RunATP, Copy Z-Matrix,
Insert, Text Import Wizard, fixed Width
Mark the second matrix below
From ATPDraw double click cable symbol, check cable constant, Press RunATP, Copy G-Matrix from Command window with ALT+Mark |  |  | , choose cable symbol, Press RunATP, Copy G-Matrix,
Insert, Text Import Wizard, fixed Width
Insert ATP Z-Matrix ohm/m here |  |  | Bergeron with CableConstants |  |  |  | Spice Matrix Reactances self and mutual for input to line_coupled.lib file
6.7624e-05 | 4.9233e-05 | 4.9232e-05 | 4.9404e-05 | 4.9233e-05 | 4.9232e-05 | + | XL11= | 0.00068802 | XM12= | 0.00042971 | XM13= | 0.00038615 | XM14= | 0.0006281 | XM15= | 0.00042971 | XM16= | 0.00038615
0.00068802 | 0.00042971 | 0.00038615 | 0.0006281 | 0.00042971 | 0.00038615 | + | XM21= | 0.00042971 | XL22= | 0.00068802 | XM23= | 0.00042971 | XM24= | 0.00042971 | XM25= | 0.0006281 | XM26= | 0.00042971
[6 empty] | + | XM31= | 0.00038615 | XM32= | 0.00042971 | XL33= | 0.00068802 | XM34= | 0.00038615 | XM35= | 0.00042971 | XM36= | 0.0006281
4.9233e-05 | 6.7624e-05 | 4.9233e-05 | 4.9233e-05 | 4.9404e-05 | 4.9233e-05 | + | XM41= | 0.0006281 | XM42= | 0.00042971 | XM43= | 0.00038615 | XL44= | 0.00062687 | XM45= | 0.00042971 | XM46= | 0.00038615
0.00042971 | 0.00068802 | 0.00042971 | 0.00042971 | 0.0006281 | 0.00042971 | + | XM51= | 0.00042971 | XM52= | 0.0006281 | XM53= | 0.00042971 | XM54= | 0.00042971 | XL55= | 0.00062687 | XM56= | 0.00042971
[6 empty] | + | XM61= | 0.00038615 | XM62= | 0.00042971 | XM63= | 0.0006281 | XM64= | 0.00038615 | XM65= | 0.00042971 | XL66= | 0.00062687
4.9232e-05 | 4.9233e-05 | 6.7624e-05 | 4.9232e-05 | 4.9233e-05 | 4.9404e-05 | + | Ce = | 3.371e-10
0.00038615 | 0.00042971 | 0.00068802 | 0.00038615 | 0.00042971 | 0.0006281 | + | Cshield = | 2.5548e-09
4.9404e-05 | 4.9233e-05 | 4.9232e-05 | 6.2204e-05 | 4.9233e-05 | 4.9232e-05 | .param rnn = | 6.7624e-05
0.0006281 | 0.00042971 | 0.00038615 | 0.00062687 | 0.00042971 | 0.00038615 | .param rmm = | { | 6.2204e-05 | / fact }
[6 empty] | .param rmn = | 4.9233e-05
4.9233e-05 | 4.9404e-05 | 4.9233e-05 | 4.9233e-05 | 6.2204e-05 | 4.9233e-05
0.00042971 | 0.0006281 | 0.00042971 | 0.00042971 | 0.00062687 | 0.00042971 | Transposed:
4.9232e-05 | 4.9233e-05 | 4.9404e-05 | 4.9232e-05 | 4.9233e-05 | 6.2204e-05 | + | XL11= | 0.00068802 | XM12= | 0.00041519 | XM13= | 0.00041519 | XM14= | 0.0006281 | XM15= | 0.00041519 | XM16= | 0.00041519
0.00038615 | 0.00042971 | 0.0006281 | 0.00038615 | 0.00042971 | 0.00062687 | + | XM21= | 0.00041519 | XL22= | 0.00068802 | XM23= | 0.00041519 | XM24= | 0.00041519 | XM25= | 0.0006281 | XM26= | 0.00041519
[6 empty] | + | XM31= | 0.00041519 | XM32= | 0.00041519 | XL33= | 0.00068802 | XM34= | 0.00041519 | XM35= | 0.00041519 | XM36= | 0.0006281
[6 empty] | + | XM41= | 0.0006281 | XM42= | 0.00041519 | XM43= | 0.00041519 | XL44= | 0.00062687 | XM45= | 0.00041519 | XM46= | 0.00041519
Insert ATP G-Matrix Farad/m here |  |  | Bergeron with CableConstants |  |  | + | XM51= | 0.00041519 | XM52= | 0.0006281 | XM53= | 0.00041519 | XM54= | 0.00041519 | XL55= | 0.00062687 | XM56= | 0.00041519
[6 empty] | + | XM61= | 0.00041519 | XM62= | 0.00041519 | XM63= | 0.0006281 | XM64= | 0.00041519 | XM65= | 0.00041519 | XL66= | 0.00062687
0 | 0 | 0 | 0 | 0 | 0
3.371e-10 | 0 | 0 | -3.371e-10 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 3.371e-10 | 0 | 0 | -3.371e-10 | 0
0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 3.371e-10 | 0 | 0 | -3.371e-10 | [9 empty] | Computation of R0 R1 X0 X1 Z0 Z1 from the Matrices (KRON REDUCTION)
0 | 0 | 0 | 0 | 0 | 0 |  |  | frequency: | 50 | [5 empty] | Rcc,0: | 0.16609 |  | Meanvalue of sum of rows | Vc0 = | Rcc,0 | Rcs,0 | * Ic,0
-3.371e-10 | 0 | 0 | 2.5548e-09 | 0 | 0 | Ls_Lm: |  | L1 | L2 | L3 | Sh1 | Sh2 | Sh3 |  | Rcs,0: | 0.14787 |  | Meanvalue of sum of rows | Vs0 = | Rsc,0 | Rss,0 | * Is,0
[7 empty] | L1 | 0.00219 | 0.0013678 | 0.0012292 | 0.0019993 | 0.0013678 | 0.0012292 |  | Rss,0: | 0.16067 |  | Meanvalue of sum of rows
0 | 0 | 0 | 0 | 0 | 0 |  | L2 | 0.0013678 | 0.00219 | 0.0013678 | 0.0013678 | 0.0019993 | 0.0013678 |  | Rsc,0=Rcs,0
0 | -3.371e-10 | 0 | 0 | 2.5548e-09 | 0 |  | L3 | 0.0012292 | 0.0013678 | 0.00219 | 0.0012292 | 0.0013678 | 0.0019993
[7 empty] | Sh1 | 0.0019993 | 0.0013678 | 0.0012292 | 0.0019954 | 0.0013678 | 0.0012292 |  | Xcc,0: | 1.5184 |  | Meanvalue of sum of rows
0 | 0 | 0 | 0 | 0 | 0 |  | Sh2 | 0.0013678 | 0.0019993 | 0.0013678 | 0.0013678 | 0.0019954 | 0.0013678 |  | Xcs,0: | 1.4585 |  | Meanvalue of sum of rows
0 | 0 | -3.371e-10 | 0 | 0 | 2.5548e-09 |  | Sh3 | 0.0012292 | 0.0013678 | 0.0019993 | 0.0012292 | 0.0013678 | 0.0019954 |  | Xss,0: | 1.4572 |  | Meanvalue of sum of rows
[6 empty] | Cs_Cm: |  | L1 | L2 | L3 | Sh1 | Sh2 | Sh3 |  | Zcc,0: | 0.166088473+1.51839906666667i
Dezimaltrennzeichen ändern vom , auf . | [6 empty] | L1 | 3.3709e-07 | 0 | 0 | -3.3709e-07 | 0 | 0 |  | Zcs,0: | 0.147868355+1.45847430666667i
In Windows zentral | [6 empty] | L2 | 0 | 3.3709e-07 | 0 | 0 | -3.3709e-07 | 0 |  | Zss,0: | 0.160668894+1.45724800666667i |  |  |  |  | for exact values of R,X see Matlab File Kron_Reduktion_1mm_transposed.m
Start / Region eingeben / Weitere Einstallungen / Zahlen | [6 empty] | L3 | 0 | 0 | 3.3709e-07 | 0 | 0 | -3.3709e-07
[7 empty] | Sh1 | -3.3709e-07 | 0 | 0 | 2.5548e-06 | 0 | 0 |  | Null-System for doubled bonding Vs,0=0 -> Z0,eff = Zcc,0 - Zcs,0*Zsc,0/Zss,0 | [5 empty] | guessed: | R0eff: | 0.03103 | X0,eff: | 0.058811
Dezimaltrennzeichen ändern vom , auf . | [6 empty] | Sh2 | 0 | -3.3709e-07 | 0 | 0 | 2.5548e-06 | 0 |  | Null-System for single bonding: Is,0=0 Z0eff=Zcc,0 | [6 empty] | R0eff: | 0.16609 | X0,eff: | 1.5184
In Excel local | [6 empty] | Sh3 | 0 | 0 | -3.3709e-07 | 0 | 0 | 2.5548e-06
Datei/Optionen/Erweitert/Dezimaltrennzeichen | [14 empty] | You can see that the zero impdeance of the cable is reduced from 1.518 ohm to 0,0588 ohm for double point bonding
[6 empty] | Rs_Rm: |  | L1 | L2 | L3 | Sh1 | Sh2 | Sh3
[7 empty] | L1 | 0.067624 | 0.049233 | 0.049232 | 0.049404 | 0.049233 | 0.049232
[7 empty] | L2 | 0.049233 | 0.067624 | 0.049233 | 0.049233 | 0.049404 | 0.049233 |  | Rcc,1: | 0.018391 |  | Meanvalue Diagonal values - Meanvalue neardiagonal values
[7 empty] | L3 | 0.049232 | 0.049233 | 0.067624 | 0.049232 | 0.049233 | 0.049404 |  | Rcs,1: | 0.0001713
[7 empty] | Sh1 | 0.049404 | 0.049233 | 0.049232 | 0.062204 | 0.049233 | 0.049232 |  | Rss,1: | 0.012972
[7 empty] | Sh2 | 0.049233 | 0.049404 | 0.049233 | 0.049233 | 0.062204 | 0.049233
[7 empty] | Sh3 | 0.049232 | 0.049233 | 0.049404 | 0.049232 | 0.049233 | 0.062204 |  | Xcc,1: | 0.28009 |  | Meanvalue Diagonal values - Meanvalue neardiagonal values
[15 empty] | Xcs,1: | 0.22017
[15 empty] | Xss,1: | 0.21894 |  |  |  | NOTE: for double bonding R0eff=R1eff X0eff=X1eff see also ATP Kronreduktion:
[6 empty] | Xs_Xm: |  | L1 | L2 | L3 | Sh1 | Sh2 | Sh3 | [6 empty] | line_cable_shield_400kV_1200mm2_1km_2_thick_shield_5mm_grounded_internally.xlsx
[7 empty] | L1 | 0.68802 | 0.42971 | 0.38615 | 0.6281 | 0.42971 | 0.38615 |  | Zcc,1: | 0.018391422+0.280093605i
[7 empty] | L2 | 0.42971 | 0.68802 | 0.42971 | 0.42971 | 0.6281 | 0.42971 |  | Zcs,1: | 0.000171303999999997+0.220168845i |  |  |  |  | for exact values of R,X see Matlab File Kron_Reduktion_1mm_transposed.m
[7 empty] | L3 | 0.38615 | 0.42971 | 0.68802 | 0.38615 | 0.42971 | 0.6281 |  | Zss,1: | 0.012971843+0.218942545i
[7 empty] | Sh1 | 0.6281 | 0.42971 | 0.38615 | 0.62687 | 0.42971 | 0.38615 | [7 empty] | guessed: | R1eff: | 0.03112 | X1eff: | 0.059446
[7 empty] | Sh2 | 0.42971 | 0.6281 | 0.42971 | 0.42971 | 0.62687 | 0.42971 |  | Positive sequence system for doubled bonding Vs,0=0 -> Z1,eff = Zcc,1 - Zcs,1*Zsc,0/Zss,1 | [6 empty] | R1eff: | 0.018391 | X1eff: | 0.28009
[7 empty] | Sh3 | 0.38615 | 0.42971 | 0.6281 | 0.38615 | 0.42971 | 0.62687 |  | Positiv sequence system for single bonding: Is,0=0 Z1eff=Zcc,1
[6 empty] | Xs_Xm_transposed | [8 empty] | Kronreduction:
[8 empty] | L1 | L2 | L3 | Sh1 | Sh2 | Sh3 |  | V=Z*I
[7 empty] | L1 | 0.68802 | 0.41519 | 0.41519 | 0.6281 | 0.41519 | 0.41519 |  | V1=Z11*I1+Z12*I2
[7 empty] | L2 | 0.41519 | 0.68802 | 0.41519 | 0.41519 | 0.6281 | 0.41519 |  | V2=Z21*I1+Z22*I2
[7 empty] | L3 | 0.41519 | 0.41519 | 0.68802 | 0.41519 | 0.41519 | 0.6281 |  | V2=0 (Earth wire grounded)
[7 empty] | Sh1 | 0.6281 | 0.41519 | 0.41519 | 0.62687 | 0.41519 | 0.41519 |  | 0=Z21*I1+Z22*I2
[7 empty] | Sh2 | 0.41519 | 0.6281 | 0.41519 | 0.41519 | 0.62687 | 0.41519 |  | I2=-Z22^-1*Z21*I1
[7 empty] | Sh3 | 0.41519 | 0.41519 | 0.6281 | 0.41519 | 0.41519 | 0.62687 |  | insert I2 in eqn1
V1=Z11*I1+Z12*(-Z22^-1*Z21*I1)
V1=(Z11-Z12*Z22^-1*Z21)*I1
Zred=(Z11-Z12*Z22^-1*Z21)
Zij_neu=Zij-Zik*Zkj/Zkk
k=node to eleminate !

## ATP-Overheadline_6phase_Pi
From ATPDraw Different_lines_400V_20kV.acp or Different_lines_110kV_1150kV , choose click cable symbol, Press RunATP, ATP Capacitance-Matrix and ATP Impedance_Matrix
Start/Einfügen/Textassistent
| Insert ATP Capacitance-Matrix Farad/km for equivalent phase conductors here | [5 empty] | Spice Matrix Reactances self and mutual , capacitances CE,CL
| Einfügen, Assistent, Feste Breite, Click für Spalten Trennen am Ende | [5 empty] | Copy and Paste to model in file coupled_lines.lib | [13 empty] | transposed:
1 | 1.0823e-08 | [5 empty] | + | R1= | 0.015 | R2= | 0.015 | R3= | 0.015 | R4= | 0.015 | R5= | 0.015 | R6= | 0.015
[7 empty] | + | XL11= | 0.47016 | [11 empty] | + | XL11= | 0.48186
2 | -1.8998e-09 | 1.1709e-08 |  |  |  |  | + | XM12= | 0.20539 | XL22= | 0.48898 | [9 empty] | + | XM12= | 0.22111 | XL22= | 0.48186
[7 empty] | + | XM13= | 0.20397 | XM23= | 0.25396 | XL33= | 0.48644 | [7 empty] | + | XM13= | 0.22111 | XM23= | 0.22111 | XL33= | 0.48186
3 | -1.6986e-09 | -3.4087e-09 | 1.2083e-08 |  |  |  | + | XM14= | 0.16735 | XM24= | 0.15996 | XM34= | 0.17365 | XL44= | 0.47016 | [5 empty] | + | XM14= | 0.17286 | XM24= | 0.17286 | XM34= | 0.17286 | XL44= | 0.48186
[7 empty] | + | XM15= | 0.15996 | XM25= | 0.16818 | XM35= | 0.18497 | XM45= | 0.20539 | XL55= | 0.48898 |  |  |  | + | XM15= | 0.17286 | XM25= | 0.17286 | XM35= | 0.17286 | XM45= | 0.22111 | XL55= | 0.48186
4 | -1.238e-09 | -4.5772e-10 | -7.7601e-10 | 1.0823e-08 |  |  | + | XM16= | 0.17365 | XM26= | 0.18497 | XM36= | 0.20912 | XM46= | 0.20397 | XM56= | 0.25396 | XL66= | 0.48644 |  | + | XM16= | 0.17286 | XM26= | 0.17286 | XM36= | 0.17286 | XM46= | 0.22111 | XM56= | 0.22111 | XL66= | 0.48186
[7 empty] | + | C11= | 1.0823e-08 | [11 empty] | + | C11= | 4.5775e-09
5 | -4.5772e-10 | -3.2112e-10 | -6.4674e-10 | -1.8998e-09 | 1.1709e-08 |  | + | C12= | 1.8998e-09 | C22= | 1.1709e-08 | [9 empty] | + | C12= | 2.3357e-09 | C22= | 4.5775e-09
[7 empty] | + | C13= | 1.6986e-09 | C23= | 3.4087e-09 | C33= | 1.2083e-08 | [7 empty] | + | C13= | 2.3357e-09 | C23= | 2.3357e-09 | C33= | 4.5775e-09
6 | -7.7601e-10 | -6.4674e-10 | -1.5476e-09 | -1.6986e-09 | -3.4087e-09 | 1.2083e-08 | + | C14= | 1.238e-09 | C24= | 4.5772e-10 | C34= | 7.7601e-10 | C44= | 1.0823e-08 | [5 empty] | + | C14= | 7.6307e-10 | C24= | 7.6307e-10 | C34= | 7.6307e-10 | C44= | 4.5775e-09
[7 empty] | + | C15= | 4.5772e-10 | C25= | 3.2112e-10 | C35= | 6.4674e-10 | C45= | 1.8998e-09 | C55= | 1.1709e-08 |  |  |  | + | C15= | 7.6307e-10 | C25= | 7.6307e-10 | C35= | 7.6307e-10 | C45= | 2.3357e-09 | C55= | 4.5775e-09
[7 empty] | + | C16= | 7.7601e-10 | C26= | 6.4674e-10 | C36= | 1.5476e-09 | C46= | 1.6986e-09 | C56= | 3.4087e-09 | C66= | 1.2083e-08 |  | + | C16= | 7.6307e-10 | C26= | 7.6307e-10 | C36= | 7.6307e-10 | C46= | 2.3357e-09 | C56= | 2.3357e-09 | C66= | 4.5775e-09
[7 empty] | .param Rnn= | 0.050519
[7 empty] | .param Rmm= | 0.050519
| Ltspice 400kV Donaumast | [5 empty] | .param Rmn= | 0.035796 |  |  |  |  | Ce_CLs: | 1 | 2 | 3 | 4 | 5 | 6
[13 empty] | 1 | 1.0823e-08 | 1.8998e-09 | 1.6986e-09 | 1.238e-09 | 4.5772e-10 | 7.7601e-10
[13 empty] | 2 | 1.8998e-09 | 1.1709e-08 | 3.4087e-09 | 4.5772e-10 | 3.2112e-10 | 6.4674e-10
[7 empty] | To transpose this line the following computation is done: | [5 empty] | 3 | 1.6986e-09 | 3.4087e-09 | 1.2083e-08 | 7.7601e-10 | 6.4674e-10 | 1.5476e-09
[13 empty] | 4 | 1.238e-09 | 4.5772e-10 | 7.7601e-10 | 1.0823e-08 | 1.8998e-09 | 1.6986e-09
[8 empty] | 0.050519 | Rself |  |  |  | 5 | 4.5772e-10 | 3.2112e-10 | 6.4674e-10 | 1.8998e-09 | 1.1709e-08 | 3.4087e-09
| Insert ATP Impedance-Matrix Ohms/km for equvivalent phase conductors here | [6 empty] | 0.035796 | Rm |  |  |  | 6 | 7.7601e-10 | 6.4674e-10 | 1.5476e-09 | 1.6986e-09 | 3.4087e-09 | 1.2083e-08
[8 empty] | 0.014723 | R |  | (edit frequency here)
1 | 0.050751 | [8 empty] | Frequency | 50 |  | XL_XMs: | 1 | 2 | 3 | 4 | 5 | 6
| 0.47016 | [11 empty] | 1 | 0.47016 | 0.20539 | 0.20397 | 0.16735 | 0.15996 | 0.17365
[7 empty] | CE1: | 4.7526e-09 |  | XL11: | 0.47016 |  | 2 | 0.20539 | 0.48898 | 0.25396 | 0.15996 | 0.16818 | 0.18497
2 | 0.035696 | 0.05035 |  |  |  |  | CE2: | 4.9747e-09 |  | XL22: | 0.48898 |  | 3 | 0.20397 | 0.25396 | 0.48644 | 0.17365 | 0.18497 | 0.20912
| 0.20539 | 0.48898 |  |  |  |  | CE3: | 4.0051e-09 |  | XL33: | 0.48644 |  | 4 | 0.16735 | 0.15996 | 0.17365 | 0.47016 | 0.20539 | 0.20397
[7 empty] | CE4: | 4.7526e-09 |  | XL44: | 0.47016 |  | 5 | 0.15996 | 0.16818 | 0.18497 | 0.20539 | 0.48898 | 0.25396
3 | 0.035788 | 0.035716 | 0.050457 |  |  |  | CE5: | 4.9747e-09 |  | XL55: | 0.48898 |  | 6 | 0.17365 | 0.18497 | 0.20912 | 0.20397 | 0.25396 | 0.48644
| 0.20397 | 0.25396 | 0.48644 |  |  |  | CE6: | 4.0051e-09 |  | XL66: | 0.48644
[7 empty] | Mean: Ce | 4.5775e-09 | CE | Mean: Lself | 0.0015338 | Lself
4 | 0.036057 | 0.035666 | 0.035774 | 0.050751 | [9 empty] | 2: Approximation of Transposed system matrix: copy to matlab | [7 empty] | Frequency: | 50
| 0.16735 | 0.15996 | 0.17365 | 0.47016 |  |  | CL12: | 1.8998e-09 |  | XM12: | 0.20539
[7 empty] | CL13: | 1.6986e-09 |  | XM13: | 0.20397 |  |  | Cs_Cm: | 1 | 2 | 3 | 4 | 5 | 6 | [5 empty] | Xs_Xm: | 1 | 2 | 3 | 4 | 5 | 6
5 | 0.035666 | 0.035623 | 0.035692 | 0.035696 | 0.05035 |  | CL14: | 1.238e-09 |  | XM14: | 0.16735 |  |  | 1 | 4.5775e-09 | 2.3357e-09 | 2.3357e-09 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 | [5 empty] | 1 | 0.48186 | 0.22111 | 0.22111 | 0.17286 | 0.17286 | 0.17286
| 0.15996 | 0.16818 | 0.18497 | 0.20539 | 0.48898 |  | CL15 | 4.5772e-10 |  | XM15: | 0.15996 |  |  | 2 | 2.3357e-09 | 4.5775e-09 | 2.3357e-09 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 | [5 empty] | 2 | 0.22111 | 0.48186 | 0.22111 | 0.17286 | 0.17286 | 0.17286
[7 empty] | CL16: | 7.7601e-10 |  | XM16: | 0.17365 |  |  | 3 | 2.3357e-09 | 2.3357e-09 | 4.5775e-09 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 |  | N O T E: |  |  |  | 3 | 0.22111 | 0.22111 | 0.48186 | 0.17286 | 0.17286 | 0.17286
6 | 0.035774 | 0.035692 | 0.035768 | 0.035788 | 0.035716 | 0.050457 | CL23: | 3.4087e-09 |  | XM23: | 0.25396 |  |  | 4 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 | 4.5775e-09 | 2.3357e-09 | 2.3357e-09 |  | If a different CL3 is used: |  |  |  | 4 | 0.17286 | 0.17286 | 0.17286 | 0.48186 | 0.22111 | 0.22111
| 0.17365 | 0.18497 | 0.20912 | 0.20397 | 0.25396 | 0.48644 | CL24: | 4.5772e-10 |  | XM24: | 0.15996 |  |  | 5 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 | 2.3357e-09 | 4.5775e-09 | 2.3357e-09 |  | CL2: | 6.2682e-10 |  |  | 5 | 0.17286 | 0.17286 | 0.17286 | 0.22111 | 0.48186 | 0.22111
[7 empty] | CL25: | 3.2112e-10 |  | XM25: | 0.16818 |  |  | 6 | 7.6307e-10 | 7.6307e-10 | 7.6307e-10 | 2.3357e-09 | 2.3357e-09 | 4.5775e-09 |  | CL3: | 1.0356e-09 |  |  | 6 | 0.17286 | 0.17286 | 0.17286 | 0.22111 | 0.22111 | 0.48186
[7 empty] | CL26: | 6.4674e-10 |  | XM26: | 0.18497
[7 empty] | CL34: | 7.7601e-10 |  | XM34: | 0.17365 |  |  | Ls_Lm: | 1 | 2 | 3 | 4 | 5 | 6
[7 empty] | CL35: | 6.4674e-10 |  | XM35: | 0.18497 |  |  | 1 | 0.0015338 | 0.00070382 | 0.00070382 | 0.00055023 | 0.00055023 | 0.00055023
[7 empty] | CL36: | 1.5476e-09 |  | XM36: | 0.20912 |  |  | 2 | 0.00070382 | 0.0015338 | 0.00070382 | 0.00055023 | 0.00055023 | 0.00055023
Dezimaltrennzeichen ändern vom , auf . | [6 empty] | CL45: | 1.8998e-09 |  | XM45: | 0.20539 |  |  | 3 | 0.00070382 | 0.00070382 | 0.0015338 | 0.00055023 | 0.00055023 | 0.00055023
In Windows zentral | [6 empty] | CL46: | 1.6986e-09 |  | XM46: | 0.20397 |  |  | 4 | 0.00055023 | 0.00055023 | 0.00055023 | 0.0015338 | 0.00070382 | 0.00070382 |  | N O T E:
Start / Region eingeben / Weitere Einstallungen / Zahlen | [6 empty] | CL56: | 3.4087e-09 |  | XM56: | 0.25396 |  |  | 5 | 0.00055023 | 0.00055023 | 0.00055023 | 0.00070382 | 0.0015338 | 0.00070382 |  | If only LM2 is used: LM2 and LM3 are both the same
[14 empty] | 6 | 0.00055023 | 0.00055023 | 0.00055023 | 0.00070382 | 0.00070382 | 0.0015338 |  | LM2=LM3: | 0.00055023
Dezimaltrennzeichen ändern vom , auf . | [6 empty] | Mean: Cl | 1.3921e-09 |  | Mean: Xm | 0.1939
In Excel local | [6 empty] | Mean:Cl123 | 2.3357e-09 | CL1 | Mean: Lm123 | 0.00070382 | LM1 |  | Rs_Rm | 1 | 2 | 3 | 4 | 5 | 6
Datei/Optionen/Erweitert/Dezimaltrennzeichen | [6 empty] | Mean:Cl456 | 2.3357e-09 | same as CL1 | Mean:Lm456 | 0.00070382 | same as LM1 |  | 1 | 0.050519 | 0.035796 | 0.035796 | 0.035796 | 0.035796 | 0.035796
[7 empty] | Mean:Cl_Rest | 7.6307e-10 | CL2 | Mean:Lm2 | 0.00055023 | LM2 |  | 2 | 0.035796 | 0.050519 | 0.035796 | 0.035796 | 0.035796 | 0.035796
[7 empty] | Mean:AllCl | 3.0987e-09 |  | Mean:Lm3 | 0.0005779 | LM3 |  | 3 | 0.035796 | 0.035796 | 0.050519 | 0.035796 | 0.035796 | 0.035796
[14 empty] | 4 | 0.035796 | 0.035796 | 0.035796 | 0.050519 | 0.035796 | 0.035796
[7 empty] | Mean Cb | 1.3874e-08 |  | L: and X: | 0.00082999 | 0.26075 |  | 5 | 0.035796 | 0.035796 | 0.035796 | 0.035796 | 0.050519 | 0.035796
[7 empty] | Mean CE | 4.5775e-09 |  | R: | 0.014723 |  |  | 6 | 0.035796 | 0.035796 | 0.035796 | 0.035796 | 0.035796 | 0.050519
[8 empty] | Per System: | Per Line:
[7 empty] | Q1: f(U*U,fn) | 1394735.0688 | 697367.5344 |  | Note: Q1 has CLLs and Ces, Ce*6 + CL1*6 + CL2*6 (3 are between L1 and L4,L2 and L5,L3 and L6 -> 0 because of zero voltage difference)
[7 empty] | Q0: f(U*U,fn) | 460177.2213 | 230088.6107
[7 empty] | I0(per line) | 1.0066 | IE: 3*I0 | 3.0197
[7 empty] | Frequency: | 50 | (do not edit here -> edit above)
[7 empty] | Voltage: | 400000
Copy and Paste to transposed model in file coupled_lines.lib
[7 empty] | Zero system self inductances, impedances, resistances (see ATP) | [6 empty] | R0= | 0.2295 | R1= | 0.014723 | R0m= | 0.10739
[7 empty] | L01 and X01 | 0.0029414 | 0.92408 | R01 | 0.12211 |  |  | L0= | 0.0046198 | L1= | 0.00085766 | L0m= | 0.0016784 | L1m= | 2.7663e-05
[7 empty] | L02 and X02 | 0.0029414 | 0.92408 | R02 | 0.12211 |  |  | C0= | 4.5775e-09 | C1= | 1.3465e-08 | C0m= | 2.2892e-09 | C1m= | 4.0875e-10
Zero system mutual inductances, impedances, resistances (see ATP)
[7 empty] | X00:(L0m*omega) | 0.0016784 | 0.52727 | R00:(R0m) | 0.10739 |  |  | Copy and Paste to transposed model in file coupled_lines.lib
[14 empty] | Rm= | 1: 0.035796; 2: Rs=; 3: 0.050519
[14 empty] | Lm1= | 0.00070382 | Lm2= | 0.00055023 | Lm3= | 0.0005779 | Ls= | 0.0015338
[14 empty] | CL1= | 2.3357e-09 | CL2= | 6.2682e-10 | CL3= | 1.0356e-09 | CE= | 4.5775e-09 | Cs= | 1.1538e-08
For 6phase line C1(from Ce,Cl)=Ce+3CL123+3CL_Rest C0=CE
1.3874e-08
[14 empty] | R0s: | 1: 0.12211; 3: R1s:; 4: 0.014723
[14 empty] | L0s: | 1: 0.0029414; 3: L1s:; 4: 0.00082999
[14 empty] | C0s: | 1: 6.8667e-09; 3: C1s:; 4: 1.3874e-08