Questions and answers for a successful simulation with the transient toolbox

- Which parameters should be present on each ltspice schematic

The lines:
.param tdv=1 tdt=1 
.param fn1=50(or 60) omega_n={2*pi*fn1}
.options vntol and abstol (default 1mV, 1uA in template.asc)

Additionally the maximal timestep for transient analysis should be between 0.1ms (higher accuracy - slower simulation) and 0.6ms (for a frequency of 50/60 Hz)

Best also choose the alternative solver  (simulate/control panel/spice/engine)

If the results of a transient simulation are nonsense, see if transformers are upside down. (wrong direction) or there is a false unit present (400Volts instead of 400Kilovolts). m=milli instead of meg=mega

- How can the steady state of a circuit be reached fast ?

The voltage sources have a parameter texp=val (oder tpwl=val). If this is set to 10ms..100ms the source voltage is rising slow to the final value at 50ms..500ms. The swing in by the transformer model can additionally be realized by the adjustment of the residual flux parameter (psi_0=val)

e.g.: If Ur=0 at the switching point psi_0=-1 leads immediately to a steady-state. psi_0=1 leads to a triplication of the Flux (maximal residual flux) and at psi_0=0 to a duplication of the flux (For Ur=max leads psi_0=0 to the steady state ).

- What can I do if the circuit does’nt converge ?

You can try to set the vntol and abstol and reltol parameters to a higher value.

- How can i access subcircuit currents and voltages in LTSpice ?

LTSpice->Tools->ControlPanel->SaveDefaults->
Save Subcircuit Node Voltages, Device Currents

- How can i see the active power (sum u*i all Pins) of a element ?

ALT+click to a LTSpice symbol -> thermometer symbol pops up. Additionally  STRG+click on the Trace leads to energy at the given period

- How can i detect the direction of the current ?

Currentresults in ltspice are always meant in direction into the pins 
By ltspice resistances, capacitor and inductances there is an arrow to display the currentflux. If you mirror the symbol at the schematic the arrow is also mirrored.

- How can i  adjust the font size for transient analysis?

Arial 10 Bold (Tools->DraftingOptions) should be the default for the transient and loadflow toolboxes

- What is to consider with LTSpice inductances ?

These have a serial resistance of 1m Ohm. This can be altered by right clicking with the mouse an set rser=0 or by changing the defaults: Tools-ControlPanel->Hacks->Always Defaults inductors to rser=0

- How can i switch the nonlinear transformer model to a linear one ?

right mouse click -> Value -> m=1

- Which parameter changes the magnetizing curve of a transformer ?

Only parameters a=val and m=val
For big transformers they are e.g m=7,9 
The m value is important for saturation

The  a value is a parameter for the rise of the lineare curve and the maximum Current
In the file Magnetisierungskurven_different_xxx.asc you can see curves with different values of a,m. The formula for the magnetizing current is:  
i1µ = i1µN * (a*(ɸ/ɸN) + (a-1)*(ɸ/ɸN)m)

i1µN and ɸN are the norm values  (for the steadystate), ɸ the actual value (peak) of the flux.
Since ɸ is a peak value the values of i1µN and ɸN are multiplied by 1.414 The result i1µ is then a peak value. The value for ɸN is sqrt(2)*Un/omega

How can i set the residual flux of a transformer model ?

With the psi_0 – parameters (see also question above)

- How is the residual flux set at arbitrary time in the transformer model ?

The capacitor of the flux integrator has at the beginning zero value . To the simulation time i like to introduce fluxvalues there is a voltagesource switched to the capacitor charging ist. The charging must be very rapid but also long enough to reach the final residual flux value. This is done by the Ron=val parameter of the switch. Time constant Tau=Ron*C is important. E.g. the switch is closed for 0.1ms so Ron should be set to 1e-5 aus. The capacitor of the integrator has 1F (1e-5*1)=0.01ms -> until 10*tau=0.1ms the capacitor is full of load. NOTE: Because of the process above sometimes voltage peaks are present at the charging timepoint.

- What is a good website for primar use of Ltspice (Tutorials) ?

http://www.simonbramble.co.uk/lt_spice/ltspice_lt_spice.htm

- How is the transformer model composed (JUSTUS) ?

The transformer model is a mixture of electrical and magnetic circuit. Therefore also magnetic quantities can be simulated. The iron lost and the leakage is  represented in the magnetic circuit. If electrical quantities like Lσ and Rfe are used in the magnetic circuit they must be converted. Also the phase shift must be considered . Thus Lσ becomes Rσ and Rfe becomes Lfe. Further : serial becomes parallel and vice versa, Resistance to conductance, voltage sources to currentsources,  T to Pi and so on.

Example:

Is Lσ used in the magnetic circuit so is it converted to Rσ ( Rσ=N²/Lσ). Furthermore  Rσ becomes in the magn. circuit a parallel branch (electrical serial)
Is Rfe is used in the magnetic circuit it is converted to Lfe (Lfe=N²/Rfe). Furthermore Lfe becomes in the magn. circuit a serial branch ( electrical  parallel )

- Guessed parameters to design a 300MVA transformer

Input Data:

U1Nenn = 400kV / 120kV

N1=1000 Windungen

I1µ = 0.5A (linear effective steady state value)

Middle ironway lm = 10m

B = 1.8T = Magnetizing value at (linear) nominal point

Follows:

Ψ1N=U1N/(ω*Wurzel(3))= 735 Vs,Wb

ɸ =  Ψ1N/N1 = 735/1000 = 0.735 Vs,Wb

B =  ɸ /A = 1.8 T -> Iron core square area: A=0.735/1.8=0.4084 m2

ϴµ = N1*I1µ = 1000*0.5 = 500 A

H*lm = N1*I1µ -> 10*H=1000*0.5 ->

H = 50 A/m

B = µ*H = µ0*µr*H -> µr = B/(H*µ0) = 1.8/(50*4*π/107) = 28600 (HIB-Core material)

Rm = ϴµ/ɸ = 500/0.735 = 680 H-1

Ψ1N = L1*I1µ -> L = 735/0.5 = 1470 H

Or:

Rm = N12/L1 = 1e6/1470 = 680 H-1

Or:

Rm = lm/(µ0*µr*A) = 10/(0.4*28600*4*π/107) = 680 H-1

Rm, ϴµ, ɸ are valid for the primary side and the secondary side oft he transformer

Rm=N12/L1=N22/L2 Oder: ϴµ =N1*I1µ=N2*I2µ Oder: ɸ=Ψ1N/N1=Ψ2N/N2

- The transformermodel from JUSTUS leads to ?

Formula for the nonlinear magnetizing current: 

 i1µ = i1µN * (a*(ɸ/ɸN) + (a-1)*(ɸ/ɸN)m)

The magnetizing curve is  specified through only two parameters a und m

Good values for transormers are e.g. :  a = 0.75 und m=9

With the assumption of i1µN=0.5A (nominal value of the magnitizing current) follows for the settled case (steady state)

for the settled case (steady state) :

ɸ/ɸN = 1 = 0.735 -> i1µ = 0.5 * (0.75*(1) + (0.25)*(1)9 ) = 0.5A

for switching on at voltage zero:

ɸ/ɸN = 2 = 1.47  -> i1µ = 0.5 * (0.75*(2) + (0.25)*(2)9 ) = 65A

for switching on at voltage zero and maximum residual flux:

ɸ/ɸN = 3 = 2.21  -> i1µ = 0.5 * (0.75*(3) + (0.25)*(3)9 ) = 2460A (more than 5*IN)

NOTE:

Since the magnetizing current is highly nonlinear the effective values above differs especially if ɸ/ɸN is >1. Therefore the effective value of the currents above gets much smaller (effective shape factor > 1.414). Especially for the ɸ/ɸN = 3 case where additionally the high voltage drop at the leakage inductance decrease the effective magnetic flux ( Input voltage gets smaller )

Furthermore :

Lm=10m  H=N1*i1µ/lm µ=B/H/µ0 Rm=N1*i1µ  L1=N12/Rm

ɸ/ɸN = 1 -> B=1.8 H=50  µ=28600 Rm=680 L=1470 H (at nominal value)

ɸ/ɸN = 2  -> B=3.6 H=6480  µ=442 Rm=44e3 L=22.7 H (at double flux)

ɸ/ɸN = 3 -> B=5.4 H=246100  µ=17.4 Rm=1.1e6 L=0.9 H (at triple flux)

Also at the triple flux is L higher than Lσ=ca.53.33Ω/314.159=0.1697H

NOTE: For exact values of H, L do a simulation (see NOTE above)

I don’t know the magn. resistance of the oiltank of the transformer but i guess it is  in the range of 3H (10-100x Lσ)

- How can i regulate (voltage, phase) of a transformer ?

For voltage regulation there is a rudimentary code (parameter l_ ). If l_=3 and stproz=1.5 than the primary voltage is increased by 4.5%. There are now two additionally models named trafo_tap_l and trafo_tap_s. They are  switched to the primary side of the transformer and allow voltage level (tap_l) and phase level(tap_s) regulation of the transformer. These models comes in two versions. First with fixed parameters (constant during simulation) and second with controlling pins (controlled the steps via a pwl source during simulation).

- Many models have alternatives – How can i switch the models in LTSpice ?

Right mouse click on the element

Line „Spicemodel“ -> Dropdownmenu opens and give you access to all the models in the same .lib File
NOTE: The pincount must match the symbol definition

Examples for alternate elements:  l or  l_int or l_flux

- How can i change the transient to a AC analysis ?

All transient voltage sources are  replaced by AC-sources. Additionally the .Tran line is replaced by a .Ac line (useful only if there are no switches and nonlinearities in the transient circuit)

- How can i detect if reactive power is transported ?

Voltage and Currents have a phase shift

- Many elements have control pins, Why ?

Many elements have control pins because during simulation parameters can be changed ( pwl source controls voltage level at the pin )

- How can i compute the leakage between two inductances

k = M/(sqrt(L1*L2))

σ = 1-(M²/(L1*L2))

σ = 1-(k²)

σ = σ1+σ2-σ1*σ2

By the transformer σ1=σ2 -> σ = 2*σ1-σ1²

Since σ1 is very small the quadratic term σ1² becomes 0  a. σ = 2*σ1 !

By the transformer L1σ = σ1*L1 und L2σ = σ1*L2
if L1σ,L1 is given σ, k is:

Example 400kV transformer:

L1σ = 0.1697H  L1=1470H ->  σ1=0.0001155 σ=0.000231 k=0.9999884

Note:

The formula above σ = 2*σ1-σ1²=1-k² has the analytic solution:

σ1=(1-k) folows L1σ=σ1*L1=(1-k)*L1 !! compare with the numerical values above!! Note also:

L=f(N2) -> ue=N1/N2 = sqrt(L1/L2)

If L1σ and L1 is given , σ1=L1σ/L1 , σ=2*σ1-σ1*σ1,  -> k=sqrt(1-σ)

- What is the value of the maximal flux in transformers and coils at different Voltages and nominal winding turn of 1000

Formula  PsiN = UN*sqrt(2)/(omega) bzw. PhiN=PsiN/N

PsiN(Primary)/N1 = PsiN(Sekundary)/N2  ident if k=1

U=10kV/sqrt(3)	PhiN=0.026

U=10kV		PhiN=0.045

U=20kV/sqrt(3)	PhiN=0.052

U=20kV		PhiN=0.090

U=110kv/sqrt(3)  	PhiN=0.286

U=110kV  		PhiN=0.495

U=220kV/sqrt(3) 	PhiN=0.572

U=220kV		PhiN=0.990

U=400kV/sqrt(3)	PhiN=1.039

- What is the time constant at RL and RC circuit ?

Tau = R.C    and  L/R

At about 10*Tau the steady state is reached

- What means the parameters tpsid and ron in the transformermodel ?

The parameter tpsid=0.1ms means the time the switch is on  of  the voltagesource parallel to the capacitor (C=1Coulomb) of the flux-integrator. This voltage source takes care of the initial flux.

Good values for 50/60Hz are tpsid=0.1ms and ron=1e-5=0.01m

The resistance is ten times higher since

Tau = R.C = 0.01m*1 = 0.01m means if  tpsid=0.1ms the capacitor is full loaded.

- How can i plot the magnetizing curve of a transformer ?

The secondary side of the transformer must be open. The primary axis of the plotwindow is switched from time to the current of the transformer. The flux (phi,psi) can now be plotted versus the primary current. The p0 (powerlost) parameter of the transformer leads to a small hysteresis

- How we can compute the charging power of a cable ?

Q0 = QCE+QCL = UN²*omega*CE + 3*UN²*omega*CL

At a cable with shield for every phase

Q0 = QCE since it is CL=0

The charching current is

I0 = Q0 / (UN*sqrt(3))

For earth fault follows

IE=3*I0 = 3*QCE/(UN*sqrt(3))

- What is the formula for Petersen and other compensating devices ?

Petersen:  Starpoint to earth

UN=110kV, IN=250A

ZN=(UN/sqrt(3))/IN

L=ZN/omega R=ZN/100 (guess)

Voltage compensation with L in deltaconnection:

UN=110kV QN=50MVAR

Q=QN/3

L = UN*UN/(Q*omega)

Linecompensation with L in wyeconnection:

UN=110kV QN=50MVAR

Q=QN/3

U=UN/sqrt(3)

L = U*U/(Q*omega)

Example : A line with CE=1000nF should be compensated by petersen.

Q0 = UN²*omega*CE = 3.8 MVAR

I0 = Q0/(UN*sqrt(3)) = 19.95A

IE = 3*I0 = 59.85A

Necessary is a petersencoil with

UN=110kV  IN=60A

Q = UN*IN*sqrt(3) leads to approx. 3.8 MVAR (see above!)

- Influence of the coupling of lines

All lines of the same transmission route influences itself.  So additionally to the selfinductance there is a mutual induction present

The mutual induction weaks the selfinduction and is stronger if the lines are  closer. If the coupling would be K=1 then whole inductance would be  zero .

In this toolbox there are coupled line elements with one, two, or four systems of lines.

The coupling matrices were computed by ATP(ATPDRAW). For the conversion to LTspice there is an excel file  present.

- How is the network impedance computed if there is the shortcircuit capacity present ?

SN = 3*IN*UN/sqrt(3)   with  IN=UN*sqrt(3)/Z  follows

SN = (3*UN*UN/(sqrt(3)*sqrt(3))/Z -> UN²/Z follows Z
Z = UN²/SN 
Example:

UN=400kV SN=40GVA=160e9/40e9=4ohm

The shortcircuit impedance is  j4 Ohm

UN=110kV SN=7.5GVA=12.1e9/7.5e9=1.613ohm

The shortcircuit impedance is j1.6 Ohm

- How can i show a saved plot in LTspice ?

Many examples have a saved plotfiles for showing traces of the simulation. If there are more than one files you can activate the PlotSettings / Open PlotSettings for additionally saved plotfiles

- How can i compute the whole capacitance of a overhead line ?

Csum = CE+3*CL

- How can i compute the reactive power of a cable ?

QC = UN*UN/XC =UN*UN*omega*Csum)

- How can i compute the reactive power of a coil?

Coils connected wye

QL = UN*UN/XL =UN*UN/(omega*XL)

- Whats the difference of wye and delta load (same resistances assumed)

P_delta = 3*P_wye

- How can i verify a simulation? 

You should always try a smaller timestep to see if the results differs